## SIL2_Checklist
Checklist Item | Owner | Due Date | Status (Yes/No/In progress) | Notes
Define Safety Requirements Specification (SRS) for each Safety Instrumented Function (SIF)
Confirm demand mode (low demand vs. high/continuous) for each SIF
Select components with proven-in-use or certification (IEC 61508/61511)
Verify architectural constraints (e.g., 1oo1, 1oo2) meet target SIL
Establish proof test procedures and intervals (TI) for all components
Document Diagnostic Coverage (DC) and Proof Test Coverage (PTC) assumptions
Consider common-cause factor (β) for redundant architectures
Define bypass/override policy and logging
Plan for maintenance, calibration, and MTTR assumptions
Create verification/validation test plan before commissioning
Implement management of change (MoC) process
Set up periodic performance review and gap log

## PFDavg_Inputs
Parameter | Value | Notes | Edit the 'Value' column. Units noted per row.
Dangerous undetected failure rate, λ_DU (per hour) | 1e-06 | Example 1e-6/h; use vendor FMEDA or field data | Simplified equations for illustration; use full IEC 61508/61511 methods for certification work.
Proof test interval, TI (hours) | 8760 | Annual = 8760 h; semi-annual = 4380 h, etc.
Diagnostic coverage, DC (0–1) | 0.6 | Fraction of dangerous failures auto-detected
Proof test coverage, PTC (0–1) | 0.9 | Fraction of dangerous failures found by proof test
Mean time to repair, MTTR (hours) [optional] | 8 | Used for repair-time terms (not in simple formula)
Common-cause factor, β (0–1) [for 1oo2] | 0.05 | Typical 0.02–0.10 depending on design/analysis
Note on B2: Named cell: lambda_DU
Note on B3: Named cell: TI
Note on B4: Named cell: DC
Note on B5: Named cell: PTC
Note on B6: Named cell: MTTR
Note on B7: Named cell: beta

## PFDavg_Calcs
Metric | Value | Formula (for reference) | Cells use named inputs: lambda_DU, TI, DC, PTC, beta
Effective λ_DU (after DC & PTC) | 4e-08 | λ_DU_eff = λ_DU × (1-DC) × (1-PTC)
PFDavg (1oo1, low demand, simplified) | 0.0001752 | PFDavg_1oo1 ≈ λ_DU_eff × TI / 2
PFDavg (1oo2, low demand, simplified) | 8.7892e-06 | PFDavg_1oo2 ≈ β×(λ_DU_eff×TI/2) + (1-β)×(λ_DU_eff×TI/2)^2

## SIL_Targets
SIL | PFDavg Range | Notes
SIL1 | 1e-2 to <1e-1 | Indicative targets for low-demand mode
SIL2 | 1e-3 to <1e-2 | Typical target for many process SIFs
SIL3 | 1e-4 to <1e-3 | Higher integrity requires stronger architecture/testing
SIL4 | 1e-5 to <1e-4 | Rare in process industries; shown for completeness